April 30, 2014

Weber County Planning Commission

2380 Washington Blvd.

Ogden, UT 84401

RE: Robert Painter Property, 1 lot

 Parcel #15-060-0064 Soil log #1550

Gentlemen:

The soil and percolation information for the above-referenced lot have been reviewed. Culinary water will be provided by Taylor West Weber Water District, an extension of an existing approved non-community water system. **A letter from the water supplier is required prior to issuance of a permit**.

DESIGN REQUIREMENTS

Anticipated ground water tables not to exceed 12 inches, fall within the range of acceptability for the utilization of a Mound Wastewater Disposal System or a Packed Bed Media System with an At-Grade drainfield as a means of wastewater disposal. Maximum trench depth is limited to 0 inches. The absorption system is to be designed using a maximum loading rate of 0.45 gal/sq. ft. /day.

Plans for the construction of any wastewater disposal system are to be prepared by a Utah State certified individual and submitted to this office for review prior to the issuance of a Wastewater Disposal permit.

Each on-site individual wastewater disposal system must be installed in accordance with R317-501 through R317-513, Utah Administrative Code, Individual Wastewater Disposal Systems and Weber-Morgan District Health Department Rules. Final approval will be given only after an on-site inspection of the completed project and prior to the accomplishment of any backfilling.

Please be advised that the conditions of this letter are valid for a period of 18 months. At that time the site will be re-evaluated in relation to rules in effect at that time.

Sincerely,

Michela Gladwell, LEHS

Environmental Health Division

801-399-7160